| Journal Name: | Asian Basic and Applied Research Journal |
| --- | --- |
| Manuscript Number: | Ms_ABAARJ_1948 |
| Title of the Manuscript: | Performance Analysis of Grid Connected Wind Turbine Generators under System Disturbances Using MATLAB |
| Type of the Article |  |

| - PART 1: Comments |  |  |
| --- | --- | --- |
|  | - Reviewer’s comment - Artificial Intelligence (AI) generated or assisted review comments are strictly prohibited during peer review. | - Author’s Feedback (It is mandatory that authors should write his/her feedback here) |
| Please write a few sentences regarding the importance of this manuscript for the scientific community. A minimum of 3-4 sentences may be required for this part. | Simulation model is developed for only PMSG and results were shown for both PMSG and DFIG Optimisation techniques nor methods are shown | - The simulation model of the DFIG is shown in pages 6 – 10, as well as Fig 4 and Table 4. |
| Is the title of the article suitable? (If not please suggest an alternative title) | yes | - Authors agrees with Reviewer’s comment |
| - Is the abstract of the article comprehensive? Do you suggest the addition (or deletion) of some points in this section? Please write your suggestions here. | Need to rewritten focusing more on the outcome | - Abstract updated as directed by the reviewer. |
| - Is the manuscript scientifically, correct? Please write here. | No | - The number of turbines making up the wind farm was missed out. This had been updated to reflect the 30 MW wind farm |
| Are the references sufficient and recent? If you have suggestions of additional references, please mention them in the review form. | Few more references can be added | - More references added as directed by the reviewer. |
| - Is the language/English quality of the article suitable for scholarly communications? | yes | Authors agrees with Reviewer’s comment |
| - Optional/General comments | The paper need to be modified - In Table-2 and Table-4 it is shown as rated power as 1.5 MW but in fig 5 and fig 7, the results show that 30MW is generated which is completely conflicting. - The rated voltage shown is Table-3 is 690V, but in fig5 and fig 7, in results it is shown as 10kV which is again a deviation and also check the current value. - What is the transformer rating? - In transient state the there will be more voltage spikes compared to steady state , the results shown in fig 7 and fig 8 are showing high values - Validation of results to be done - Results to be tabulated - need adequate information about the results - Forward and reverse voltage shown in tabke-2 is 100 kV which is not realistic - Control of DFIG simulation block is not shown - Optimisation techniques nor methods are shown | 1. Table 2 and 4 updated to include the number of turbines that made up the 30MW wind farm 2. Right, Figures 1 & 4 has a step-up transformer connecting the turbines to an 11kV grid network, the reason for this voltage. In addition, the fault simulation is on the grid side not on the wind turbine 3. The step-up transformer is rated 40MVA 0.69/11kV 4. Authors wish to provide some clarification on this: Figures 5 & 6 are plot of steady state with current in the range of 2kA; while Figures 7 & 8 are for transient conditions with higher current 20KA for PMSG and 7kA for DFIG. On the voltage profiles during transient state, the introduction of high fault current will first cause voltage collapse/dip before it starts recovering as seen in Figures 7 & 8. 5. Point 4 above provides explanation for the results shown on Figures 5 – 8 6. Tabulated results (Tables 5 & 6) comparing the performance of PMSG and DFIG added 7. Point 4 above provides explanation for the results shown on Figures 5 – 8 8. 1E5 was a typo-error. Voltage corrected to 1.05kV 9. DFIG control block added as Figure 4b. 10. The optimization was shown on step 6 of the control algorithms for PMSG and DFIG; So, is already embedded on the results |

| PART 2: |  |  |
| --- | --- | --- |
|  | - Reviewer’s comment | - Author’s Feedback (It is mandatory that authors should write his/her feedback here) |
| Are there ethical issues in this manuscript? | (If yes, Kindly please write down the ethical issues here in detail) no | There are no ethical issues on the manuscript |